DRY PACK GROUT

{Note to Specifier: This add-in specification component specifies Euclid Chemical Company, NS GROUT- Non-Metallic, Non-Shrink Grout.}

DRY PACK GROUT is designed for use where high-strength, non- shrink characteristics are required. DRY PACK GROUT contains only natural aggregate and is designed to be mixed with minimum water for placement at damp pack consistency for placement where flowable, fluid or plastic grouts are not possible or desired.

{Note to Specifier: The paragraphs below are meant to be incorporated into Parts 2 and 3 of a standard CSI 3 Part Format specification, project’s General Structural Notes or directly onto the plans. They must be carefully reviewed by a qualified design professional and edited to meet the particular requirements of the project at hand, assure compliance with any governing building codes, and coordinate with other specification sections and drawings.}

1.1	QUALITY REQUIREMENTS

A.	Manufacturer: ISO 9001 quality certified as primary manufacturer of specified products.

1.2	INFORMATIONAL SUBMITTALS

A.	Product List: List manufacturer name and product name for each product proposed for

use as epoxy grout.

B.	Manufacturer Certificate: Indicating products listed on Contractor's Product List are compatible and suitable for the specified application.

PART 2- PRODUCTS

2.1	MANUFACTURERS

A.	Manufacturer: Provide listed products of Euclid Chemical Co., Cleveland, OH; www.euclidchemical.com.

B.	Manufacturer Single Source: Provide cementitious grout products from a single qualified manufacturer.

2.2	CEMENTITIOUS GROUT

A.	Cementitious Grout:  Cementitious grout for high performance applications.

1.	Product shall conform to:

a)	CRD C621, US Army Corps of Engineers Specification for Non-Shrink Grout

b)	ASTM C1107, Standard Specification for Packaged, Dry, Hydraulic-Cement Grout (non-shrink)

2.	Basis of Design Product:

a)	“DRY PACK GROUT” by The Euclid Chemical Company

b)	Compressive Strength, ASTM C109 Modified to ASTM C1107 Section 11.5, 2 in. (5 cm) cubes @ 75oF (24oC), 50% RH):

1)	Dry pack consistency:

a)	1 day: 5500 psi (37.9 MPa)

b)	3 days: 6500 psi (44.8 MPa)

c)	7 days: 7000 psi ( 48.2 MPa)

d)	28 days: 8000 psi (55.2 MPa)

PART 3- EXECUTION

{Note to Specifier: This section covers surface preparation, form preparation, mixing, placement, curing, and cleanup for Euclid Chemical’s DRY PACK GROUT. For complete current instructions and safety information, consult the Technical Data and Material Safety sheets posted at www.euclidchemical.com.  The contractor and engineer are encouraged to consult and review the Euclid Chemical bulletin: “Cementitious Grout Application Guide”:

- (http://euclidchemical.com/fileshare/ProductFiles/MiscProductFiles/grout_instructions.pdf.

- The document offers instructions detailing the general installation of Euclid Chemical manufactured cement-based grout products. Important: If the contractor is not familiar with standard grout placement techniques, a pre-job meeting is suggested to review the project details unique to the particular job. Contact your local Euclid Chemical representative for additional information}

- 3.1	SURFACE PREPARATION

- A.	All surfaces to be in contact with grout shall be clean and free from rust, grease or oil.

- B.	Saturate area to be grouted with water until it is uniformly damp. Remove excess water just before placing grout.

- 3.2	MIXING

- A.	All grouting materials shall be 50°F to 80°F (10°C to 27°C) immediately prior to mixing.

- B.	Mix grout in accordance with manufacturer’s written instructions. Mix small quantities with

- a drill and "jiffy" mixer. Use a paddle type mortar mixer for large jobs.

- C.	Charge mixing vessel with appropriate amount of clean, potable water for batch size and then add dry grout. Do not exceed water content recommended by manufacturer. Control water content. Do not add admixtures, sand or cement to grout.

- D.	Mix for a minimum of 2 to 3 minutes.

- 3.3	PLACEMENT

- A.	Place grout in accordance with manufacturer’s written instructions. Do not place to move baseplates out of critcal alignment.

- 3.4	FINISHING

- A.	Finish grout in accordance with manufacturer’s written instructions. Remove forms as soon as grout has stiffened or set sufficiently to prevent sagging. Cut back shoulders and finish to desired texture where required.

- 3.5	CURING

- A.	Cure grout in accordance with manufacturer’s written instructions.

- B.	Wet cure for 24 hours. Following 24-hour wet cure, seal all surfaces with two (2) coats of a high solids curing compound.

- 3.6	CLEAN UP

- A.	Tools and mixer may be cleaned with water.